## Manual
USER INSTRUCTION MANUAL
Distribution Electrification Cost & Design Estimator (ABCDE Model)
1. PURPOSE OF THIS MODEL
This model is designed to convert high-level electrification assumptions into a consistent estimate of network infrastructure requirements and total project cost, with specific emphasis on cost per connection as the primary decision metric. The model supports planning, comparison of design approaches, and early-stage investment discussions, and should not be interpreted as a detailed engineering design tool.
2. GENERAL APPROACH
The model operates by linking a defined number of service connections to standardized distribution network relationships, from which it derives the required lengths of low-voltage and medium-voltage lines, the number and sizing of transformers, and associated infrastructure quantities. These quantities are then combined with user-defined unit costs to calculate total capital expenditure and cost per connection in a transparent and reproducible manner.
3. HOW TO USE THE MODEL
The user is required to enter all assumptions in the designated input section only, including the number of connections, density-related parameters, technical design ratios, and unit costs for each infrastructure component. Once inputs are provided, the model will automatically calculate all quantities and costs without the need for any manual intervention, and the user should refrain from modifying any calculation cells to preserve the integrity of the model.
4. INTERPRETATION OF RESULTS
The outputs of the model present a consolidated view of infrastructure quantities and associated costs, with cost per connection serving as the principal indicator for evaluating different scenarios. The user should interpret these results as planning-level estimates that provide direction and comparative insight rather than final values for implementation, and should use them to assess the financial implications of design choices and rollout strategies.
5. SCENARIO ANALYSIS
The model is structured to allow rapid testing of alternative assumptions by adjusting one or more input parameters and observing the resulting changes in outputs. Users are encouraged to modify variables such as density, transformer sizing, or unit costs individually in order to understand their specific impact on overall cost, thereby enabling a more informed and disciplined approach to planning.
6. KEY DRIVERS OF COST
The model reflects typical distribution system characteristics in which low-voltage networks and service connections represent the largest share of total cost, and where increases in technical design standards or reductions in customer density can significantly increase cost per connection. Users should pay particular attention to these drivers when evaluating results, as small changes in these parameters can have a disproportionate effect on project affordability.
7. LIMITATIONS OF THE MODEL
This model does not perform detailed engineering calculations such as load flow analysis, voltage drop assessment, or protection coordination, and it does not incorporate spatial routing or GIS-based optimization. It is intended strictly as a planning and estimation tool and should be complemented by detailed engineering studies before implementation decisions are finalized.
8. GOOD PRACTICE
Users should maintain a clear record of input assumptions for each scenario tested, avoid overwriting formulas or structural elements of the model, and use separate copies of the model for different analyses to ensure traceability. It is recommended that results be reviewed in the context of local conditions and validated against available benchmarks or previous project experience.
9. FINAL NOTE
The strength of this model lies in its ability to make the relationship between design, density, and cost explicit and measurable, thereby supporting more transparent and economically grounded electrification planning decisions. Proper use of the model will improve the quality, consistency, and credibility of investment planning across a wide range of electrification contexts.

## Input
MASTER BUDGET | Input | Explanation
Total Potential Connections | 500000
COMPONENTS | $/u
Service Connections & Meter | 150 | $100 = Low $ 200= High
Ready Boards | 50 | $40 = Low $ 100= High
Service Connection Lite Poles | 120 | $80 = Low $ 120= High
LV lines km | 10000 | $5000 = Low $ 12000= High
Transformer Stations | 12000 | $4000= Low $ 10000= High
MV lines -kilometers | 25000 | $10000 = Low $ 30000= High
Streetlights | 80 | $30 = Low $ 100= High
COMPONENTS | $/u
Service Connections & Meter | na | Includes Prepaid Meter
Ready Boards | 30% | Percemtage ready boards of total connetions
Service Connection Lite Poles | 4 | Connections per pole
LV lines km | 50 | Connections per km LV lines
Transformer Stations | 200 | 200 conn/unit
MV lines -kilometers | 800 | m/tfr
Streetlights | 4
CONNECTION TYPE | $/u
A - Sercive Connection & Ready Board | 20%
B- A plus Lite Pole | 10%
C- B-plus LV Line | 10%
D - C plus Transformer | 20%
E - D plus MV Line | 40%

## Model
CONNECTION TYPE -->> COMPONENT V | A | B | C | D | E
Total Potential Connections | No-Pole | One - Pole | LV line | Tranf. | MV line |  |  |  | Scaling
500000 | 20% | 10% | 10% | 20% | 40% | Total | Unit Cost | Total Cost | 1 | 100%
Service Connections | 100000 | 50000 | 50000 | 100000 | 200000 | 500000 | 150 | 75000000 |  | Includes Prepaid Meter
Ready Boards | 30000 | 15000 | 15000 | 30000 | 60000 | 150000 | 50 | 7500000 | 30%
Service Connection Lite Poles |  | 12500 | 12500 | 25000 | 50000 | 100000 | 120 | 12000000 | 4 | 1/conn
LV lines - km |  |  | 1000 | 2000 | 4000 | 6200 | 10000 | 62000000 | 50 | Con/km
Transformer Installations |  |  |  | 500 | 1000 | 1500 | 12000 | 18000000 | 200 | 200 conn/unit
MV lines -kilometers |  |  |  |  | 800 | 800 | 25000 | 20000000 | 800 | m/tfr
Streetlights | [5 empty] | 125000 | 80 | 10000000 | 4 | 100
Other costs
Cost per category | 16500 | 9750 | 19750 | 45500 | 111000 |  |  | 204500000 | -2000
Acc. Cost per conn | 165 | 195 | 395 | 455 | 555 |  |  | 409
Note on K8: HP: Number of connections per service pole
Note on K10: HP: Number of connections per transformer
Note on K11: HP: Number of connection per MV km of line

## Output
CONNECTION TYPE -->> COMPONENT
Total Potential Connections
500000 | Total | Unit Cost | Total Cost
Service Connections | 500000 | 150 | 75000000
Ready Boards | 150000 | 50 | 7500000
Service Connection Lite Poles | 100000 | 120 | 12000000
LV lines - km | 6200 | 10000 | 62000000
Transformer Installations | 1500 | 12000 | 18000000
MV lines -kilometers | 800 | 25000 | 20000000
Streetlights | 125000 | 80 | 10000000
Others |  |  |  | s
Total Cost |  |  | 204500000
Cost per connection |  |  | 409
CONNECTION TYPE | Percent of Total | Number | Acc. Cost per conn
A - Sercive Connection plus Ready Board | 20% | 100000 | 165
B- A plus Lite Pole | 10% | 50000 | 195
C- B-plus LV Line | 10% | 50000 | 395
D - C plus Transformer | 20% | 100000 | 455
E - D plus MV Line | 40% | 200000 | 555
Total | 100% | 500000 | 409